{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Total Electrical Load"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Total Electrical Load","index":0,"n_rows":104,"n_cols":10,"rows_kept":104,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["DIANA Total Electrical Load",{"$nulls":7},"2009-07-25"]
[{"$nulls":8},"WLW"]
[]
[]
[null,"Source of information","QTY","V","phase","I (A)","P (W)","P (W) total","VA asuming PF=0.85"]
["Vacuum system"]
["cryopumps","CTI Cryo-Torr 8",6,0,0,0,0,0,0]
["cryopump compressors","CTI 9600",6,208,3,15.3,5511.9168,33071.5008,38907.648]
["turbopumps","Pfeiffer TMU 521 P",6,0,0,0,0,0,0]
["turbopump controllers","Pfeiffer DCU 300",6,120,1,5,600,3600,4235.294117647059]
["ion gauges","MKS 943",6,120,1,0.1,12,72,84.70588235294117]
["heater tapes","Omega 1\" x 10'",6,120,1,4.4,528,3168,3727.0588235294117]
["roots blowers","from Matthaeus",2,208,3,11.1,3998.8415999999993,7997.683199999999,9409.039058823528]
["roughing pumps","Pfeiffer DUO 20 M",6,120,1,10,1200,7200,8470.588235294117]
["isolation valves","MDC",6,0,0,0,0,0,0]
["valve controllers","LBNL blue box - 13W4892",6,120,1,1,120,720,847.0588235294118]
["RGA","SRS PPR 300",2,120,1,2.5,300,600,705.8823529411765]
[]
[{"$nulls":7},"SUB TOTAL",66387.27529411764]
[]
["HVPS (400kV, 100mA)"]
["HVPS","Kaiser preliminary spec, 80% efficient",1,480,3,61,50712.96,50712.96,59662.30588235294]
["misc","guess",1,120,1,10,1200,1200,1411.764705882353]
[]
[{"$nulls":7},"SUB TOTAL",61074.07058823529]
[]
["Dynamitron (3MV, 10mA)"]
["HVPS","IBA, assume 80% efficient",1,480,3,46,38242.56,38242.56,44991.24705882353]
["misc","guess",1,120,1,10,1200,1200,1411.764705882353]
[]
[{"$nulls":7},"SUB TOTAL",46403.01176470588]
[]
["Low Energy Magnets"]
["magnet #1 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #2 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #3 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #4 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #5 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #6 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #7 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #8 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #9 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #10 PS","1T solenoid, from VENUS",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #11 PS","analyzing magnet",1,208,3,30,10807.68,10807.68,12714.917647058825]
[]
[{"$nulls":7},"SUB TOTAL",726706.4470588233]
[]
["High Energy Magnets"]
["magnet #1 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #2 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #3 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #4 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #5 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #6 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #7 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #8 PS","quadrupole, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
["magnet #9 PS","steering magnet, probably high",1,480,3,73,60689.28,60689.28,71399.15294117646]
[]
[{"$nulls":7},"SUB TOTAL",642592.376470588]
[]
["Low Energy Ion Source"]
["RF power supply","guess",1,208,3,6,2161.536,2161.536,2542.9835294117647]
["misc","guess",1,120,1,10,1200,1200,1411.764705882353]
[]
[{"$nulls":7},"SUB TOTAL",3954.748235294118]
[]
["High Energy Ion Source"]
["RF power supply","guess",1,208,3,6,2161.536,2161.536,2542.9835294117647]
["misc","guess",1,120,1,10,1200,1200,1411.764705882353]
[]
[{"$nulls":7},"SUB TOTAL",3954.748235294118]
[]
["Control System"]
["oscilloscopes ","Tektronix",2,120,1,4.6,552,1104,1298.8235294117646]
["digitizer system","National Instruments and Agilent",1,120,1,50,6000,6000,7058.823529411765]
["computers","Dell T5500",2,120,1,7.4,888,1776,2089.4117647058824]
["trigger generators","SRS DG-645 or BNC 575",1,120,1,3,360,360,423.5294117647059]
[]
[{"$nulls":7},"SUB TOTAL",10870.588235294119]
[]
["Diagnostics"]
["detector electronics","guess",6,120,1,20,2400,14400,16941.176470588234]
["bias power supplies","guess",6,120,1,1.25,150,900,1058.8235294117646]
["misc","guess",1,120,1,10,1200,1200,1411.764705882353]
[]
[{"$nulls":7},"SUB TOTAL",19411.764705882353]
[]
["Miscellaneous"]
["alignment system","NDCX-I system",1,120,1,20,2400,2400,2823.529411764706]
["interlock system","guess",1,120,1,2.1,252,252,296.47058823529414]
["crane","facilities"]
["AC","facilities"]
["water cooling","facilities"]
["lighting","facilities"]
[]
[{"$nulls":7},"SUB TOTAL",3120]
[]
[]
[]
[{"$nulls":7},"TOTAL",1584475.030588235,"VA"]
[]
[{"$nulls":7},"TOTAL",1584.475030588235,"KVA"]
[]
[{"$nulls":6},"TOTAL with 20% safety factor",null,1901.370036705882,"KVA"]